**Performance analysis and optimization of a combined cooling and power system using low boiling point working fluid driven by engine waste heat**

Wenge Huang, Jiangfeng Wang\*, Jiaxi Xia, Pan Zhao, Yiping Dai

Institute of Turbomachinery, Shaanxi Engineering Laboratory of Turbomachinery and Power Equipment, State Key Laboratory of Multiphase Flow in Power Engineering, School of Energy and Power Engineering, Xi’an Jiaotong University, Xi’an 710049, China

**Corresponding author:** Jiangfeng Wang

**Mailing address:**

Institute of Turbomachinery, Shaanxi Engineering Laboratory of Turbomachinery and

Power Equipment, State Key Laboratory of Multiphase Flow in Power Engineering,

School of Energy and Power Engineering

Xi’an Jiaotong University, Xi’an 710049, China

E-mail address: jfwang@mail.xjtu.edu.cn (JF Wang).

# Performance analysis and optimization of a combined cooling and power system using low boiling point working fluid driven by engine waste heat

Wenge Huang, Jiangfeng Wang\*, Jiaxi Xia, Pan Zhao, Yiping Dai

Institute of Turbomachinery, Shaanxi Engineering Laboratory of Turbomachinery and Power Equipment, State Key Laboratory of Multiphase Flow in Power Engineering, School of Energy and Power Engineering, Xi’an Jiaotong University, Xi’an 710049, China

**Abstract**

This paper develops a combined cooling and power system, which consists of a carbon dioxide Brayton cycle, a dual-pressure organic Rankine cycle and an ejector refrigeration cycle, to recover waste heat from exhaust gas and jacket water in internal combustion engines. Thermodynamic models of the system are performed and exergoeconomic methods are used to calculate the levelized exergy cost of the component products. Effects of seven parameters, including temperature and pressure at the Brayton cycle turbine inlet, temperature and pressure at the high-pressure and low-pressure side of the organic Rankine cycle turbine inlet and pressure at the ejector primary inlet, are evaluated. Single-objective optimization is carried out by means of genetic algorithm to obtain the minimum levelized exergy cost of system product. Results show that the increase of pressure at Brayton cycle turbine inlet and high-pressure and low-pressure side of the organic Rankine cycle turbine inlet contributes to the decrease of levelized exergy cost of the system product. Optimization shows that minimum levelized exergy cost for system product is 53.25 $ (MWh)-1. When levelized exergy cost is minimum, system net power output, cooling capacity and exergy efficiency are 374.37 kW, 188.63 kW and 37.31%, respectively.

**Nomenclature**

|  |  |  |  |
| --- | --- | --- | --- |
| Latin symbols | | ρ | density, kg m-3 |
| A | area, m2 | μ | dynamic viscosity, m2 s-1 |
| Bo | boiling number | η | efficiency, % |
| c | levelized average cost, $ (MWh)-1 | δ | thickness, m |
| cp | specific heat, kJ kg-1 K-1 | Subscribes | |
| C | cost rate, $ year-1 | 1-31 | state points |
| D | diameter, m | g1-g3 | state points |
| e | exergy, kJ kg-1 | w1-w3 | state points |
| E | exergy flow rate, kJ s-1 | Bt | Brayton cycle turbine |
| Ey | exergy flow rate per year, kJ year-1 | BM | bare module |
| F | multiplying factor | cond | condenser |
| f | friction factor | comp | compressor |
| G | mass flow rate, kg s-1 | D | destruction |
| h | enthalpy, kJ kg-1 | elec | electricity |
| H | depth, m | es | equivalent diameter |
| ieff | interest rate | ev | evaporation/evaporator |
| l | length, m | ex | exergy |
| M | mass flow rate, kg s-1 | F | fuel |
| n | lifetime, year | g | exhaust gas |
| Nu | Nusselt number | gh | gas heater |
| P | pressure, MPa | he | heat exchanger |
| Pr | Prandtl number | L | loss |
| Pt | center distance between tubes, m | l | liquid |
| Pr | reduced pressure | M | material |
| Q | heat transfer rate, kW | Ot | ORC turbine |
| Qcool | cooling capacity, kW | P | product |
| qm | average imposed wall heat flux, W m-2 | p1 | pump 1 |
| rf | enthalpy of vaporization, kJ kg-1 | p2 | pump 2 |
| T | temperature, K | p3 | pump 3 |
| U | overall heat transfer coefficient, W m-2 K-1 | p4 | pump 4 |
| W | power, kW | pf | primary flow |
| Wy | annually power, MWh year-1 | prec | precooler |
| x | vapor quality | preh | preheater |
| Z | annually levelized cost value, $ year-1 | s | shell |
| z | capital cost, k$ | t | tube |
| Acronyms | | th | thermal |
| BC | Brayton cycle | turb | turbine |
| CBC | CO2 Brayton cycle | vg | vapor generator |
| CCP | combined cooling and power | w | tube wall |
| CRF | capital recovery factor |  |  |
| CEPCI | chemical engineering plant cost index |  |  |
| DORC | dual-pressure organic Rankine cycle |  |  |
| ERC | ejector refrigeration cycle |  |  |
| GA | genetic algorithm |  |  |
| TEG | thermoelectric generator |  |  |
| AARC | ammonia absorption refrigeration cycle |  |  |
| Greek symbols | |  |  |
| α | convection heat transfer coefficient, W m-2 K-1 |  |  |
| λ | heat conductivity, W m-1 K-1 |  |  |

## Introduction

Nowadays, internal combustion engine (ICE) is the major motive power source in energy field, which are widely used in transport, construction, agriculture, etc. Over 49 % of the total transportation fuel is consumed by ICEs [1]. However, only 30-45% of the fuel energy is converted into effective power output, while the remaining energy is discharged to the environment via exhaust gas, jacket water and charge air, causing a large amount of waste fuel energy [2]. Thus, technology for waste heat recovery from ICEs has drawn much interest of researchers in the last decade. Much effort has been devoted to the study of organic Rankine cycle (ORC) based ICE waste heat recovery system for its advantages of high efficiency and simple structure [3].

There are two important pathways that will lead to the improvement of the ORC system for ICE waste heat recovery. One will be selecting organic working fluids which are suitable for the system under certain conditions. Another is to optimize the system configuration to make full use of the waste heat.

The work of selecting suitable organic working fluids for ORC was carried out by many researchers to improve the efficiency of the ICE waste heat recovery. Lu et al. [4] evaluated the performance of six different working fluids in a small-scale ORC system for ICE waste heat recovery. Rijpkema et al. [5] compared the performance of twelve working fluids in an ORC-based ICE waste heat recovery system to find the suitable candidate. Su et al. [6] developed a theoretical efficiency model about working fluids selecting for ORC-based ICE waste heat recovery system via strict mathematical derivation.

Configuration optimization in ORC-based ICE waste heat recovery system mainly focuses on reducing the system irreversible rate to fully utilize the engine waste heat. Vaja and Gambarotta [7] added a preheater and a recuperator separately to a simple ORC system to improve the performance for the ICE waste heat recovery. Kim et al. [8] proposed a novel single-loop ORC system to recovery engine waste heat. They employed two recuperators in series to heat the working fluid. Comparison showed that the net power output of the system was 35.6% more than simple ORC system. Because that the maximum power output of single-loop ORC is lower than that of the dual-loop ORC system [9], more attention has been focused on dual-loop ORC based ICE waste heat recovery system in recent years. Wang et al. [10] modeled a dual-loop ORC system for engine waste heat recovery. The high-temperature loop absorbed heat from exhaust gas and its residual heat acted as heat source for the low-temperature loop. Wang et al. [11] investigated a dual-loop ORC system for ICE waste heat recovery. The high-temperature loop absorbed heat from exhaust gas for the first time. Then the low-temperature loop absorbed heat from the residual heat of the exhaust gas to realize the cascading utilization of the waste heat. Huang et al. [12] proposed a complex dual-loop ORC system for engine waste heat recovery. The high-temperature loop absorbed heat from the exhaust gas and residual heat from both the exhaust gas and the high-temperature loop provided heat for the low-temperature loop.

When referring to heat transfer in the high-temperature loop, thermal stability of organic working fluid is necessary to be considered. In previous studies, refrigerants were most selected as working fluids. The decomposition temperatures of refrigerants are relatively low (200-300 ℃) [13], while the temperature of exhaust gas is above 450 ℃ [14]. Direct heat transfer between high-temperature exhaust gas and refrigerant caused the risk of working fluid decomposition. Though high decomposition temperature working fluids such as siloxanes and alkanes were adopted by some researchers, their flammability hindered their further applications [15]. Though placing a heat transfer oil intermediate loop between the exhaust gas and the ORC system could address this issue [16], it would cause a large amount of the high-temperature waste heat unharnessed. Therefore, some other high-temperature loops for waste heat recovery were employed by researchers to couple with the ORC. Miller et al. [17] introduced thermoelectric generator (TEG) technology. High-temperature exhaust gas was first exploited by the TEG, then the cooled exhaust gas could drive the ORC safely. But the energy conversion capacity of TEG is low because of the material limitation. Steam Rankine for its high efficiency and stable operation attracted much attention of researchers. Shu et al. [18] placed a steam Rankine cycle between the ORC and the exhaust gas. Yu et al. [19] coupled a steam Rankine cycle with an ORC for the ICE waste heat recovery. However, the large bulk of the components in steam Rankine cycle limits further applications (such as application in vehicles) [20]. Considering the requirement of high thermal efficiency and compact configuration, Brayton cycle could be a compromise solution. Brayton cycle with CO2 (carbon dioxide) as working fluid has the advantage of low environmental impact and good thermodynamic performance [21]. Few studies about ORC system coupled with CO2 Brayton cycle (CBC) for ICE waste heat recovery have been published. Though Zhang et al. [20] carried out some relevant studies, their attention was focused on comparing the performance of CBC, TEG and steam Rankine cycle when coupled with the same bottom ORC. Detailed analysis of the CBC was not given and the energy in jacket water was not harnessed.

Jacket water, though containing large amounts of energy [22], obtained little attention in the previous studies. For its relatively low temperature, jacket water was mainly used to preheat the organic working fluid in the ORC system. In the ORC-based ICE waste heat recovery system designed by Zhang et al. [23] jacket water was used to preheat the organic working fluid. Then the organic working fluid was heat by the high-temperature exhaust gas to vapor state and expanded in the ORC turbine. In Yang’s [24] ICE waste heat recovery system, jacket water and secondary exhaust gas were used to preheat the organic working fluids in ORC. In the dual-loop ORC based ICE waste heat recovery system investigated by Song et al. [25], jacket water was used to preheat the low-temperature-loop. Yu et al. [26] calculated the energy recovery efficiency from an ORC-based ICE waste heat recovery system. 75% waste heat could be recovered from the exhaust gas, while only 9.5% waste heat was recovery from jacket water. The relatively low utilization rate of jacket water in the ORC system is caused by the mismatch of working fluid mass flow rate in the preheater and the evaporator. Thus, the utilization of energy in jacket water could be further explored.

Multigeneration system driven by waste heat has drawn increasing interest of researchers in light of the trend towards reducing emissions, increasing the efficiency of energy use and providing variable energy. Li et al. [27] modeled a combined cooling, heating and power system to highly utilize the waste heat. Yari et al. [28] proposed a waste heat recovery system to provide power, distilled water and heat. Bai et al. [29] investigated a cooling, heating and power system driven by exhaust gas to recovery the waste heat. Combined cooling and power (CCP) systems driven by ICE waste heat were also investigated by some researchers. Chen et al. [30] designed an ammonia-water combined cooling and power system using the waste heat from the ICEs. Ammonia-water was heated by exhaust gas and jacket water. One part of the ammonia-water vapor flew into the turbine to provide power and the other part flew into the evaporator to provide refrigeration. Salek et al. [31] coupled an ammonia absorption refrigeration cycle and a bottoming Rankine cycle with internal combustion engine to produce power and cooling capacity.

Ammonia absorption refrigeration cycle (AARC) were widely used in the combined cooing and power system for its larger refrigeration output. However, the complex cycle structure and high driven temperature requirement of AARC might sometimes limit its applications. On the contrary, ejector refrigeration cycle (ERC) exhibits the advantages of easy maintenance and high reliability [32] and it can be driven by low-temperature heat source such as the jacket water. Thus, ICE waste heat recovery system with ERC driven by jacket water not only simultaneously generate power and refrigeration but also fully utilized the jacket water waste heat.

In this study, a combined cooling and power system is developed, which comprises a CO2 Brayton cycle, a dual-pressure organic Rankine (DORC) cycle and an ejector refrigeration cycle. The CO2 Brayton cycle absorbs heat from the high-temperature exhaust gas directly to prevent the decomposition risk. The turbine exhaust in the CO2 Brayton cycle and the engine exhaust gas after heat transfer are respectively regarded as the heat sources for the high-pressure side and low-pressure side of the dual-pressure ORC, realizing the cascading utilization of exhaust gas. Meanwhile, organic working fluids in high-pressure side and low-pressure side are both preheated by jacket water which increases the mass flow rate of the organic working fluid preheated by jacket water. What’s more, the ejector refrigeration cycle is adopted to produce refrigeration and fully utilize waste heat in jacket water. Thermodynamic and exergoeconomic analysis is carried out to examine the effects of key parameters on system performance. Then a system optimization is conducted to obtain the minimum levelized exergy cost for the system product by means of genetic algorithm (GA).

The innovative features of this paper are as follow:

* A CO2 Brayton cycle is investigated to prevent the risk of decomposition of organic working fluid and provide power.
* A novel dual-pressure ORC system is developed to cascading utilize the waste heat in exhaust gas and jacket water and provide large amounts of power output.
* An ejector refrigeration cycle driven by jacket water is designed to provide refrigeration and fully utilize the jacket water waste heat.

## System description

* 1. ~~CCP system~~

The combined cooling and power system is shown in Fig. 1. The system integrates a dual-pressure organic Rankine cycle with a CO2­ Brayton cycle and an ejector refrigeration, which can produce power and refrigeration simultaneously. High-temperature gas heat from the ICE enters the gas heater to provide heat for the CBC. In the CBC, compressor compresses the CO2 to a supercritical state. The high-pressure CO2 flows into the gas heater to absorb heat. Then CO2 with high temperature and high pressure expands through the BC turbine to produce power.

After expanding in the BC turbine, the high-temperature exhaust CO2 flows into vapor generator 2 to heat the organic working fluid. High-pressure side organic working fluid heated by the CO2 then flows into the ORC turbine to produce power. Meanwhile low-pressure side organic working fluid absorbs heat from the secondary engine exhaust gas in vapor generator 1 and then enters ORC turbine to produce power.

Exhaust vapor from the ORC turbine is cooled by condenser 1 to liquid state and pressured by pump 1. Jacket water with large mass flow rate is used to preheat the organic working fluid in the preheater. The preheated organic working fluid then separates. One part of the fluid is pumped by pump 3 to the vapor generator 1 to cycle in the low-pressure side. The other part is pumped by pump 2 to the vapor generator 2 to cycle in the high-pressure side.

The jacket water then flows into vapor generator 3 to provide heat for the ejector refrigeration cycle. After the condensation process in condenser 2, liquid working fluid is divided into two separated parts. One part of the fluid is pumped to the vapor generator 3 to absorb heat from jacket water and then becomes superheated vapor. The other part of the working fluid flows through the throttle valve to become low-pressure vapor-liquid mixture. The low-pressure mixture enters the evaporator to produce cooling capacity when absorbing heat from the environment and become low-pressure vapor. After that, the superheated vapor mixes with the low-pressure vapor in the ejector. The mixed working fluid enters the condenser 2 to be condensed to liquid.

R245fa is selected as the working fluid for the organic Rankine cycle and the ejector refrigeration cycle because of the great thermodynamic performance [33] and the low environment effects [34].

## System model

~~Several assumptions are made to simplify the simulation of the system.~~

~~(1) The system keeps a steady state.~~

~~(2) The heat and friction losses in the system are not considered.~~

~~(3) The pressure losses in the vapor generator, preheater, precooler, evaporator and condenser are neglected.~~

~~(4) Considering the low gas acid dew point temperature, the gas temperature at the outlet of the vapor generator 1 is higher than 110℃ [31].~~

~~(5) The working fluid out of the condensers and preheater is saturated liquid and the state at the outlet of the evaporator is saturated vapor.~~

~~(6) The process through the throttle valve is isenthalpic.~~

Several assumptions are made to simplify the simulation of the system, which are: (1) the system keeps a steady state; (2) the heat and frication in the system are not considered; (3) the pressure losses in the vapor generators, preheater, evaporator, condensers and pipes are neglected; (4) the gas temperature at the outlet of the vapor generator 1 is higher than 110 ℃ [35], considering the low gas dew point temperature; (5) the working fluids at the outlet of the condensers and the preheater are saturated liquids, and the evaporator outlet state is saturated vapor; (6) the process through the throttle valve is isenthalpic.

~~3.1. Thermodynamic model~~

### Energy model

The net power of the CO2 Brayton cycle is expressed as:

 (1)

The net power of the DORC is given as:

 (2)

The cooling capacity of the ERC is given as:

 (3)

The net power output of the whole system is calculated as:

 (4)

The thermal efficiency of the system is given as:

 (5)

The detailed energy model equations of each component are list in Table 1. Note that there are two expanding processes in the ORC turbine. ~~The high-pressure side vapor expands from high pressure (state 10) to low pressure (state 11) for the first time and then mixes with the low-pressure side vapor. After that, the mixed vapor expands from low pressure (state 11) to the back pressure of ORC turbine (state 12) for the secondary time.~~ The high-pressure vapor expands in the turbine and then mixes with the vapor from vapor generator 1. After that, the mixed vapor expands in the turbine for the second time.

### Exergy model

~~In general, the energy model of a system is based on the first law of the thermodynamic which focuses the amount of the thermal energy in the system. The exergy model of the system is based on the second law of the thermodynamic which focuses on the quality of the thermal energy. The exergy analysis of the system is based on a dead state (the ambient conditions in this paper). The equation of exergy for unit working fluid is expressed as:~~

The energy model of the system is based on the first law of thermodynamics. From the viewpoint of the first law, it is equivalent for work and heat. Nevertheless, according to the second law of the thermodynamics, the irreversibility of work and heat is different. The exergy is used to quantifies the difference between them. The exergy model of the system is based on a dead state (the ambient condition in this study). Definition of exergy is given as:

 (6)

where h0, T0 and s0 are the parameters under the ambient conditions.

The exergy flow rate in this study is given by:

 (7)

In this study, all the components in the system are associated directly or indirectly with fuel of other heat sources, such as exhaust as and jacket water ~~in this study~~. The heat sources provide exergy for the components to operate. For each component, there is an exergy balance equation, being expressed as [36]:

 (8)

where EF, EP, ED­, EL donate the rate of exergyfor the component fuel, the rate of exergyfor component product, the rate of component exergy destruction and the rate of component exergy loss, respectively.

The details of the exergy balance equations for each component are listed in Table 1.

The exergy efficiency represents the degree of the utilization of the waste heat in the system, being expressed as:

 (9)

where Ecool is the exergy rate of the cooling process, being expressed as:

 (10)

~~3.2. Capital cost and exergoeconomic model of the system~~

### Capital cost calculation

~~In this study, a method of modeling the capital costs of the main component is employed [33]. At first, the bare module cost of the components is calculated as the basic cost.~~ A method of modeling the capital costs of main components is used in this study. According to Ref. [37], the bare module cost of the components is calculated as the basic cost. The basic cost of the components includes the direct project cost (such as component cost, material cost of the installation, etc.) and the indirect project cost (like the taxes, insurance engineering expenses, etc.). The bare module cost of the components is calculated under basic conditions. For deviations from the based conditions, multiplying factors (the specific component type, the specific system pressure and the specific material of construction) are added in the calculation to correct the results. In the following text, equations from Eq. (11) to Eq. (21) are proposed in Ref. [37].

Axial turbines (BC turbine and ORC turbine) are used in this study. The bare module cost equation of the turbine is:

 (11)

where ~~K~~~~turb~~ ~~is constant corresponding to~~ Ki, turb are constants corresponding to the turbine type; and W is the power output of the turbine.

Turbines used in this study are made of carbon steel (CS) and operate under high pressure. Thus, a multiplying factor is used to correct the result. The capital cost of the turbine is given as:

 (12)

where FBM,turb is the multiplying factor corresponding to the working conditions of the turbine.

Reciprocating pumps are used in this study. The bare module cost equation of the pumps is given as:

 (13)

where ~~K~~~~pump~~ ~~is constant corresponding to~~ Ki, pump are the constants corresponding to the pump type; and W is the power input of the pump.

Pumps used in this study are made of stainless steel (SS) and work under high pressure. Thus, multiplying factors are used to correct the bare module cost. The capital cost of the pump is given as:

 (14)

where ~~B~~~~pump~~ ~~is constant corresponding to~~ Bi, pump are the constants corresponding to the type of the pump; FM,pump is the material factor of the pump and FP,pump is the pressure factor of the pump. The equation of the pressure factor is given as:

 (15)

where ~~C~~~~pump~~ ~~is the constant corresponding to~~ Ci, pump are the constants corresponding to the type of the pump; and Ppump is the pressure of the pump under working conditions.

Axial compressor is used in this study. The bare module cost equation of the compressor is given as:

 (16)

where ~~K~~~~comp~~ ~~is the constant corresponding to~~ Ki,comp are the constants corresponding to the type of the compressor; W is the power input of the compressor.

The compressor is made of carbon steel (CS) and works under high pressure.

Correction equation of the bare module cost is given as:

 (17)

where FBM,comp is the constant corresponding to the type of the compressor.

~~Tube-and-shell~~ Shell-and-tube heat exchangers (gas heater, vapor generators, precooler, preheater, evaporator and condensers) are used in this study. The bare module cost equation of the heat exchanger is given as:

 (18)

where ~~K~~~~he~~ ~~is the constant corresponding to~~ Ki,he are the constants corresponding to the type of the heat exchanger; A is the heat transfer area of the heat exchanger. The calculation of the heat exchanger areas is presented in Appendix A.

Heat exchangers used in this study are made of carbon steel (CS) and work under different pressure. Multiplying factors are needed to correct the results, the equation is given as:

 (19)

where ~~B~~~~he~~ ~~are the constants correspond to~~ Bi,he are the constants corresponding to the type of the heat exchanger. FM,he and FP,he are the material factor and pressure factor, respectively. The pressure factor is obtained from the following equation:

 (20)

where ~~C~~~~he~~ ~~is the constant corresponding to~~ Ci,he are the constants corresponding to the type of the heat exchanger; Phe is the designed working pressure for the heat exchanger.

The values of the constants mentioned above for the main components are listed in Appendix B.

The calculation of the bare module cost depends on past records or published correlations for price information. It is necessary to update the costs because of the inflation. This can be achieved by the following equation:

 (21)

where C is the purchased cost and I is the cost index. The subscript 1 refers to base time when cost is known and subscript 2 refers to time when cost is desired. The CEPCI (Chemical Engineering Plant Cost Index) is employed to calculate the inflation. The values of CEPCI2016 and CEPCIref,2001 are 541.7 and 397, respectively ~~[34,35]~~ [38].

### Exergoeconomic model

Exergoeconomic is a branch of engineering which combines the thermodynamic analysis and economic principles. Thermodynamic performance and economic cost of the system are all taken into consideration.

To find the relationship between the present value of the expenditure and the equivalent annually levelized costs, the capital recovery factor (CRF) is employed, being expressed as [36]:

 (22)

 (23)

where ieff is the effective discount rate with a value of 0.05 [39]; and n is the lifetime of the CCP system, being assumed as 30 years [40].

In order to calculate the equivalent annually levelized costs, the annual working time of the system is assumed as 8000 h [41]. Then the annual exergy rates and annual power output or consumption are obtained.

In a steady system, there are a number of entering and outing working fluid streams and heat and work interactions with the surroundings. In exergoeconomic analysis, each flowing stream is associated with a levelized exergy cost. The equations to calculate the cost of the stream product are given as:

 (24)

 (25)

 (26)

 (27)

where c denotes levelized exergy cost of the streams; Ey,in and Ey,out are the exergy transfer rate of the stream flowing in and out of a component; Wy and Ey,heat are the power and the heat transfer rate of the components considering the annual working time.

The cost balance equation applied to the kth system component is given as:

 (28)

Details of the cost balance equation are listed in Table 2.

The levelized exergy cost for system product is chosen to indicate the exergoeconomic performance, being expressed as [42,43]:

 (29)

where ccapital is the capital-cost-related part of the levelized exergy cost for the system product, being expressed as:

 (30)

where cfuel is the fuel-cost-related part of the levelized exergy cost for the system product, being expressed as:

 (31)

where cBt and cOt are the levelized exergy cost for the BC turbine power output and the ORC turbine power output, which are calculated in Table 3. Likewise, they can be expressed as the capital-cost-related part and the fuel-cost-related part, given by Eq. (32) and Eq. (33).

 (32)

 (33)

In addition, the levelized exergy cost for the condensers and the precooler is equal to zero, being given by:

c26=c28=c30=0 (34)

The levelized exergy cost for the exhaust gas as well as the jacket water is zero, being expressed as:

cg1=cw1=0 (35)

### Internal combustion engine

In this study, the engine selected [7] is a 12-cylinder 4-stroke supercharged engine. The main designed parameters of the engine are listed in Table 3. The composition of the engine exhaust gas is presented in Table 4. The thermal load of the engine exhaust gas is about 1700 kW and 1000 kW can be obtained from the engine jacket water.

### Simulation conditions for the system

The thermodynamic parameters of the working fluid are calculated under the environment of MATLAB with the help of REFPROP 9.1 [44]. The basic conditions of simulation for the CCP system are listed in Table 5.

Seven key parameters : BC turbine inlet temperature (TBt,in), BC turbine inlet pressure (PBt, in), inlet temperature at the high-pressure side of ORC turbine (TOt, in, h), inlet pressure at the high-pressure side of ORC turbine (POt, in, h), inlet temperature at the low-pressure side of ORC turbine (TOt, in, l), inlet pressure at the low-pressure side of ORC turbine (POt, in, l) and the ejector primary inlet pressure (Pej, in), are chosen to analyze the thermodynamic and exergoeconomic performance of the system. When one parameter is investigated to analyze the system performance, other parameters are maintained constants based on the conditions in Table 5.

In the thermodynamic aspect, the net power output of the CO2 Brayton cycle (W BC), net power output of the DORC (W ORC), net power of the whole system (W net), cooling capacity of the system (Qcool) and the exergy efficiency of the system () are selected to reflect the system performance. Levelized exergy cost for the BC turbine power output (cBt), levelized exergy cost for the ORC turbine power output (cOt), levelized exergy cost the system product (cproduct) and the system capital cost (zcapital) are chosen to represent the exergoeconomic performance.

## Results and discussion

~~4.1.1.Simulation conditions for the system~~

~~The thermodynamic parameters of the working fluid are calculated under the environment of MATLAB with the help of REFPROP 9.1 [41]. The basic conditions of simulation for the CCP system are listed in Table 3~~

~~4.1.2.Internal combustion engine~~

~~In this study, the engine selected [8] is a 12-cylinder 4-stroke supercharged gas engine. The main designed parameters of the engine are listed in Table 4. The composition of the engine exhaust gas is presented in Table 5. The heat load capacity of the engine exhaust gas is about 1700 kW when cooled down to the acid dew temperature and the 1000 kW can be obtained from the engine jacket water.~~

~~4.2. Analysis for the thermodynamic and exergoeconimic performance~~

~~Seven key parameters (BC turbine inlet temperature, BC turbine inlet pressure, inlet temperature at the high-pressure side of ORC turbine, inlet pressure at the high-pressure side of ORC turbine, inlet temperature at the low-pressure side of ORC turbine, inlet pressure at the low-pressure side of ORC turbine and the ejector primary inlet pressure) are chosen to analyze the thermodynamic and exergoeconomic performance of the system. In the thermodynamic aspect, the net power output of the CO~~~~2~~ ~~Brayton cycle (W~~ ~~BC~~~~), net power output of the DORC (W~~ ~~ORC~~~~), net power of the whole system (W~~ ~~net~~~~), cooling capacity of the system (Q~~~~cool~~~~) and the exergy efficiency of the system () are selected to reflect the system performance. Levelized exergy cost for the BC turbine power output (c~~~~Bt~~~~), levelized exergy cost for the ORC turbine power output (c~~~~Ot~~~~), levelized exergy cost the system product (c~~~~product~~~~) and the system capital cost (z~~~~capital~~~~) are chosen to represent the exergoeconomic performance.~~

~~4.2.1.Variations of thermal parameters in CBC~~

The influence of the BC turbine inlet temperature (TBt,in) on the output and the exergy efficiency of the system are shown in Fig. 2. The net power output of the CBC increases with the rise of TBt,in. That can be explained by the large decrease of the compressor power consumption. ~~With the increase of the CO~~~~2~~ ~~temperature at the BC turbine inlet, the mass flow rate of CO~~~~2~~ ~~decreases.~~ ~~As a result, less CO~~~~2~~ ~~working fluid is compressed by the compressor, leading to the decrease of the compressor power consumption. On the one hand, the decrease of the mass flow rate cuts down the BC turbine power output. On the other hand, the increase of inlet temperature causes the increase of enthalpy drop of CO~~~~2~~ ~~in the turbine which results in the increase of the BC turbine power output. The two effects mention above cause the slight decrease of the BC turbine power output, which is smaller than the decrease of the compressor power consumption. Thus, the large decrease of the compressor power consumption determines the increase of the CBC net power output.~~ With the increase of the CO2 temperature at the BC turbine inlet, the mass flow rate of CO2 decreases, leading to the decrease of the compressor power consumption. Although the drop of CO2 mass flow rate would cut down the BC turbine power output, the decrease quantity of compressor power consumption is larger than the decrease of the BC turbine power output. Thus, the large decrease of the compressor power consumption determines the increase trend of the CBC net power output.

It is presented that the net power output of the DORC increases with the rise of the BC turbine inlet temperature. Since the residual heat in exhaust CO2 acts as the heat source for the high-pressure side of DORC, the temperature rise of the exhaust CO2, caused by the rise of TBt,in, would offer more heat for the bottom cycle, which causes the increase of the mass flow rate of the organic working fluid in the high-pressure side of DORC . Hence, the power output of the ORC turbine increases, leading to the increase of the net power output of the DORC.

With the increase of TBt,in, the cooling capacity of the ERC decreases, as shown in Fig. 2. ~~As discussed above, the increase of the exhaust CO~~~~2~~ ~~temperature causes the increase of the organic working fluid mass flow rate in DORC. Thus, more heat is absorbed by the organic working fluid in the preheater from the jacket water.~~ The increase of the organic working fluid mass flow rate in DORC would absorb more heat from jacket water, resulting in the decrease of energy available for the ERC. As a result, less secondary flow working fluid from the evaporator is entrained to the ejector, resulting the decrease of the cooling capacity of the CCP system.

The increase of the CBC net power output and the DORC net power output account for the increase of the net power output of the whole CCP system. ~~That can be explained by the increase of the CO~~~~2~~ ~~Brayton cycle net power output and the DORC net power output. The increase of the net power output of the system causes the increase of the exergy efficiency of the system.~~ Though the cooling capacity of the ERC is large, it produces only a small amount of exergy. The decrease of the exergy output caused by the refrigeration capacity decrease can be made up by the increase of the power exergy output. Thus, the exergy efficiency of the system increases.

The influences of the BC turbine inlet temperature on the levelized exergy cost and the system capital cost of the system are shown in Fig. 3. The levelized exergy cost for the BC turbine power output (cBt) drops with the rise of the BC turbine inlet temperature (TBt,in). ~~Since the decrease of the compressor power consumption, the cost of compressor decreases. According to Eq. (32), the decrease of compressor cost leads to the decrease of capital-cost-part of the levelized exergy cost for the BC turbine power output c~~~~Bt~~~~. Thus, c~~~~Bt~~ ~~decreases. The levelized exergy cost for the ORC turbine decreases with the increase of the BC turbine inlet temperature. The reason for this is the large increase of the power output of the ORC turbine. The increase of the ORC turbine power output causes the increase of both the capital-cost-related part and fuel-cost-related part of c~~~~Ot~~~~.~~ That can be explained by the decrease of the capital-cost-related part of cBt. The capital-cost-related part of cBt decreases with the decrease of cost of compressor, which is cut down by the drop of the compressor power consumption. The increase of the ORC turbine power output causes the decrease of both the capital-cost related part and the fuel-cost-related part of cOt, resulting in the decrease of cOt.

The system capital cost (zcapital) rises with the rise of TBt,in. The large increase of the ORC turbine power output increases the cost of the ORC turbine. Moreover, the increase of the mass flow rate of the organic working fluid in the DORC causes the increase of cost for the vapor generator 2 and the preheater. Though the cost of compressor decreases, it can’t change the ascending trend of the total system capital.

It can be obtained in Fig. 3 that the levelized exergy cost for the system product (cproduct) decreases with the rise of TBt,in. ~~As mentioned above, the levelized exergy cost for the BC turbine and ORC turbine decrease. Analyzing from Eq. (31), the fuel-cost-related part of the levelized exergy cost for system product decreases. According to Eq. (30), the increase of system net power output causes the decrease of the capital-cost-related part of the levelized exergy cost for the system product. As a result, the levelized exergy cost for the system product decreases.~~ The decline in levelized exergy cost for the BC turbine and ORC turbine power output, according to Eq. (31), would cause the decrease of the fuel-cost related part of cproduct. Though the increase of zcapital would cut down the capital-cost-related part of cproduct, the impact of levelized exergy cost for the BC turbine and ORC turbine is greater, which leads to the descending trend of cproduct.

The influence of the BC turbine inlet pressure (PBt, in) on the output and the exergy efficiency of the system are shown in Fig. 4. The net power output of the CBC increases with the increase of PBt, in, which can be explained by the rise of enthalpy drop of the CO2 in the BC turbine. Though the rise of PBt, in requires more compressor power consumption, the increase of the BC turbine power output is larger in quantity than the consumption, which leads to the increase of the CBC net power output.

The net power output of the DORC decreases with the rise of PBt, in. On the one hand, the temperature of the exhaust CO2 at the BC turbine outlet decreases with the increase of PBt, in. Thus, less heat is offered to the high-pressure cycle of DORC, resulting in the decrease of the high-pressure cycle power output. On the other hand, the increase of PBt, in causes the increase of the compressor power consumption, which results in the rise of the CO2 temperature at the compressor outlet. Thus, less heat is released in the gas heater and more heat is provided to the low-pressure cycle of DORC, which leads to the increase of the low-pressure cycle power output. However, the increase of the power output in low-pressure side is smaller than the decrease of the power output in the high-pressure side. Thus, the net power of the DORC decreases slightly.

The cooling capacity of the system increases with the increase of PBt, in. ~~The decrease of the mass flow rate in the high-pressure side of DORC is more than the increase of the mass flow rate in the low-pressure side.~~ Just like the variation of the power output, the decrease of the mass flow rate in the high-pressure side of DORC is larger than the increase of mass flow rate in the low-pressure side. Therefore, the total mass flow rate in the DORC decreases, resulting in the reduction of heat provided for the ejector refrigeration cycle. Thus, the cooling capacity of the ERC decreases.

The net power output of the whole system increases with the increase of the BC turbine inlet pressure. Though the net power output of the DORC decreases, the increase of CBC net power output is much larger. Thus, the net power output of the CCP system increases with the increase of PBt, in. The exergy efficiency of the system likewise has the same rising trend.

The influences of the BC turbine inlet pressure (PBt, in) on the levelized exergy cost and the system capital cost of the system are depicted in Fig. 5. The levelized exergy cost for the BC turbine output cBt increases with the rise of the PBt, in, which can be explained by the variations of the capital-cost-related part and the fuel-cost-related part. ~~Meanwhile, the increase of the compressor power consumption causes the increase of the levelized exergy cost for the CO~~~~2~~ ~~at the turbine inlet, resulting in the increase of the fuel-cost-related part of c~~~~Bt~~~~. As a result, c~~~~Bt~~ ~~increases.~~ The increase of PBt, in causes the increase of cost for both the BC turbine and the compressor, which lead to the rise of the two related parts.

The levelized exergy cost for the ORC turbine product (cOt) increases with the rise of PBt,in. The decrease of the mass flow rate in the DORC causes that less exergy is produced in vapor generator 2, causing the increase of the fuel-related part of cOt. Therefore, the levelized exergy cost for the ORC turbine (cOt) increases.

The system capital cost (zcapital) increases with the rise of (PBt, in). The increase of the mass flow rate in the ERC causes the rise of capital cost for the evaporator and vapor generator 3, which combined with the rise of the BC turbine cost and compressor cost accounts for the system capital cost rise.

The levelized exergy cost for the system product decreases with the rise of PBt, in as presented in Fig. 5. According to Eq. (31), the rise of the cOt, cBt would cause the rise of the fuel-cost-related part of cproduct. However, because of the large increase of the system net power output, the capital-cost-related part and the fuel-cost-related part decrease actually, which determines the decrease of cproduct.

~~4.2.2.Variations of thermal parameters in DORC.~~

The influence of inlet temperature at the high-pressure side of ORC turbine (TOt, in, h) on the output and the exergy efficiency of the system are shown in Fig. 6. The net power output of the CBC remains unchanged since thermal parameters in dual-pressure ORC are irrelevant to the thermodynamic performance of the CBC.

The net power output of the DORC decreases with the increase of TOt, in, h. ~~With the increase of the vapor temperature at the high-pressure ORC inlet, the mass flow rate of the organic working fluid in the high-pressure side of DORC decreases. The decrease of organic working fluid mass flow rate causes the decrease of the power output of the ORC turbine, which further causes the decrease of the net power output of the DORC.~~

Though the increase of the vapor temperature could lead to the rise of the enthalpy drop in the ORC turbine, it would also cause the decrease of the mass flow rate in the high-pressure side, whose impact is greater than that of the enthalpy drop. Therefore, the power output of the DORC decreases.

The cooling capacity of the ejector refrigeration cycle increases with the rise of TOt, in, h. More heat is provided for the ERC because of the decrease of the mass flow rate in the DORC, leading to the increase of the mass flow rate in vapor generator 3. Thus, more secondary flow from the evaporator is entrained into the ejector, resulting in the increase of the cooling capacity.

The net power output of the CCP system decreases with the rise of TOt, in, h. ~~The decrease of the organic working fluid mass flow rate in the DORC results in the decrease of the heat transfer rate in the preheater. More heat is released in vapor generator 3 from the jacket water to the working fluid in the ejector refrigeration cycle, leading to the increase of the working fluid mass flow rate. Consequently, the cooling capacity of the ejector refrigeration cycle increases.~~ The unchanged CBC power output and the drop of the DORC power output determine the decrease of the net power output of the CCP system. The exergy efficiency of the system as well drops with the increase of the increase of TOt, in, h.

The influences of inlet temperature at the high-pressure side of ORC turbine on the levelized exergy cost and the system capital cost of the system are presented in Fig. 7. The levelized exergy cost for the ORC turbine output (cOt) increases with the increase of TOt, in, h. ~~The can be explained by the decrease of the decrease of the ORC turbine power output.~~ The reason is that the two related parts of cOt increase with the drop of the ORC turbine power output.

The levelized exergy cost for the BC turbine power output (cBt) increases with the rise the TOt, in, h. Since the decrease of the mass flow rate in the high-pressure side of DORC, the exergy generated in the vapor generator 2 decreases, causing the increase of the levelized exergy cost of the vapor. Thus, the increase levelized exergy cost of the vapor, which is heated by the BC turbine residual heat, causes the increase of the levelized exergy cost for the exhaust CO2. According to Eq. (32), the fuel-cost-related part of cBt increases, leading to the increase of cBt.

The system capital cost (zcapital) decreases with the increase of TOt, in, h. The decrease of the DORC power output causes the drop of the ORC turbine cost, which leads to the descending trend of zcapital.

The levelized exergy cost for the system product (cproduct) increases with the rise of TOt, in, h, as shown in Fig. 7. The increase of the levelized exergy cost for the BC turbine and ORC turbine power output cause the rise of fuel-cost-related part of cproduct. Meanwhile, the large decrease of the net power of the CCP system causes the increase of the capital-cost-related part. The two increase parts determine the rise of cproduct.

The influences of the inlet pressure at the high-pressure side of ORC turbine (POt, in, h) on the output and exergy efficiency of the system are presented in Fig. 8. The net power of the CBC keeps unchanged because of the unchanged thermal parameters in the cycle.

The net power output of the DORC increase with the rise of POt, in, h. The increase of the evaporation pressure cuts down the latent heat of the organic working fluid, which causes the increase of the mass flow rate in the high-pressure side of DORC. As a result, the net power output of the ORC turbine increases, leading to the increase of the net power output of the DORC.

Considering the increase of the DORC net power output and the unchanged CBC net power output, the net power output of the whole system increases. Also, the exergy efficiency of the system increases.

The increase of the mass flow rate in the DORC absorbs more heat from the jacket water in the preheater. Thus, less heat is released in the vapor generator 3, causing the decrease of the mass flow rate of the working fluid in the ERC. As a result, the cooling capacity of the system decreases.

The influence of the inlet pressure at the high-pressure side of the ORC turbine (POt, in, h) on the levelized exergy cost and system capital cost of the system are presented in Fig. 9. The large increase of the ORC turbine power output accounts for the decrease of the levelized exergy cost for the ORC turbine power output (cOt). ~~The levelized exergy cost for the vapor at the vapor generator 2 outlet decreases. The exhaust CO~~~~2~~ ~~of the BC turbine provides heat for the vapor. The decrease of the vapor levelized exergy cost causes the decrease of the exhaust CO~~~~2~~ ~~levelized exergy cost. Meanwhile, the decrease of the levelized exergy cost for the CO~~~~2~~ ~~causes results in the decrease of the fuel-cost-related part of the levelized exergy cost for the BC turbine output. As a result, the levelized exergy cost for the BC turbine power output decreases.~~ The increase of the mass flow rate in the high-pressure side of DORC means that more exergy in the vapor is generated by the vapor generator 2, which leads to the decrease of its levelized exergy cost. Thus, the levelized exergy cost for the BC turbine exhaust CO2, which provides heat for the vapor, decreases with the vapor levelized exergy cost. Moreover, the drop of the CO2 levelized exergy cost causes the decrease of the fuel-cost-related part of cBt, which further results in the decrease of cBt.

The increase of the ORC turbine power output and the increase of mass flow rate in the DORC cause the increase of cost for the turbine and the vapor generator 2, leading to the rise of the system capital cost.

The levelized exergy cost for the system product (cproduct) decreases with the increase of POt, in, h. The decrease of cOt and cBt account for the decrease of the fuel-cost-related part of the levelized exergy for the system product. The impact of cOt and cBt is greater than that of the system capital cost whose rise would result in the increase of the capital-cost-related part of cproduct. Thus, the levelized exergy cost of the system product (cproduct) shows a descending trend.

The influences of the inlet temperature at the low-pressure side of ORC turbine (TOt, in, l) on the output and the exergy efficiency of the system are presented in Fig. 10. Parameters changes in the DORC are irrelevant to the thermodynamic performance of the CBC. Thus, the net power of the CBC remains unchanged.

The net power output of the DORC decreases with the increase of TOt, in, l. The increase of the inlet temperature causes the decrease of the mass flow rate in the low-pressure side of the DORC, leading to the decrease of the DORC net power output.

Considering the decrease of the DORC net power output and the unchanged CBC net power output, the net power output of the whole system deceases. Likewise, the exergy efficiency of the system decreases.

The cooling capacity of the ejector refrigeration cycle increases with the increase of TOt, in, l. The decrease of the mass flow rate in the low-pressure side means that more heat is offered to the ERC. Thus, the mass flow rate of the working fluid in the vapor generator 3 increases and more working fluid is entrained to the ejector from the evaporator, which leads to the increase of the refrigeration cycle.

The influence of inlet temperature at the low-pressure side of the ORC turbine (TOt, in, l) on the levelized exergy cost and system capital cost of the system are presented in Fig. 11. The levelized cost for the BC turbine power output increase with the increase of TOt, in, l. ~~Though the enthalpy of the organic working fluid increases with the increase of the low-pressure side inlet temperature, the decrease of the mass flow rate causes the decrease of the exergy provided by the vapor generator 1. Thus, the levelized exergy cost of the vapor generated by vapor generator 1 increases. The levelized exergy cost for vapor in vapor generator 2 is the equal to the levelized exergy cost for vapor in vapor generator 1. As a result, the levelized exergy cost for the vapor generator 2 vapor increases, causing the increase of the levelized exergy cost of the exhaust CO~~~~2~~ ~~after the BC turbine. The increase of the levelized exergy cost for the exhaust CO~~~~2~~ ~~causes the increase of the levelized exergy cost of the BC turbine power output.~~ The decrease of the mass flow rate in the vapor generator 1 leads to the drop of the vapor exergy output, which results in the increase of the levelized exergy cost for the vapor. The levelized exergy cost for vapor in vapor generator 2, which is the equal to that of the vapor in vapor generator 1, increases as a result, causing the increase of the levelized exergy cost of the exhaust CO2 after the BC turbine. Thus, the fuel-cost-related part of cBt increases, resulting in the rise of cBt.

The levelized exergy cost for the ORC turbine (cOt) increases with the increase of TOt, in, l. ~~As mentioned above, the levelized exergy cost for the vapor at the low-pressure side of ORC turbine inlet increases. Thus, the fuel-cost-related part of the levelized exergy cost for the ORC turbine output increases. Also, the decrease of the ORC turbine power output causes the increase both the fuel-cost-related part and the capital-cost-related part. As a result, the levelized exergy cost for the ORC turbine power output increases.~~ That can be explained by the increase of the levelized exergy cost of the ORC low-pressure inlet vapor and the decrease of the power output of the ORC turbine power output. Both the fuel-cost-related part and the capital-cost-related part of cOt increases.

The decrease of the mass flow rate and the ORC turbine power output cause the decrease of the vapor generator 1 cost and the turbine cost. Thus, the capital cost of the system decreases.

The levelized exergy cost for the system product increases with the increase of TOt, in, l. The increase of cBt and cOt cause the increase of the fuel-cost-related part of the levelized exergy cost for the system product. Though, the decease of the system capital cost causes the decrease of the capital-cost-related part, its effect is less important. Thus, the increase of the fuel-cost-related part determines the increase of the levelized exergy cost for the system product.

The influences of the inlet temperature of the low-pressure side of the ORC turbine (POt, in, l) on the output of the exergy efficiency of the system are shown in Fig. 12. The net power of the CBC keeps unchanged with the increase of the increase of the low evaporation pressure. The reason is that the thermodynamic of the CBC is irrelevant to the thermal parameters in DORC.

The net power output of the DORC increases with the rise of POt, in, l. The increase of enthalpy drop of the organic working fluid in the low-pressure side, which is caused by the rise of POt, in, l, results in the increase of the power output of the low-pressure side. Though mass flow rate in the low-pressure side would decrease, its impact is less important than that of the enthalpy drop. Thus, the net power output of DORC increases.

The unchanged CBC power output and the increase of the DORC power accounts for the increase of the system net power output and exergy efficiency of the system.

The cooling capacity increases slightly with the increase of POt, in, l. Because of the decrease of the mass flow rate in DORC, less heat is released in the preheater and more heat is provided in vapor generator 3. Thus, the mass flow rate of the working fluid in the ERC increases, resulting in the slight increase of the cooling capacity.

The influences of inlet pressure at the low-pressure side of the ORC turbine (POt, in, l) on the levelized exergy cost and system capital cost of the system are shown in Fig. 13. The levelized exergy cost for the ORC turbine power output decreases with the increase of POt, in, l. That can be explained by the decrease of the vapor generator 1 cost, caused by the decrease of the mass flow rate in DORC, and the increase of the DORC power output. Both the capital-cost-related part and the fuel-cost-related part of cOt decrease.

The levelized exergy cost for the BC turbine power output decreases with of POt, in, l.

The decrease of the cOt causes the drop of levelized exergy cost for the vapor in vapor generator 2, which is heated by the residual heat in the BC turbine exhaust CO2. Thus, the levelized exergy cost of the exhaust CO2 decreases, which further leads to the drop of the fuel-cost-related part of cBt. Therefore, the levelized exergy cost for the BC turbine power output (cBt) decreases, as shown in Fig. 13.

The increase of the ORC turbine power output causes the increase of the ORC turbine cost. Meanwhile, the increase of the cooling capacity causes the increase of the heat transfer area in the evaporator which requires the rise of the evaporator cost. Thus, the capacity cost of the system increases.

The levelized exergy cost for the system product decreases with the increase of POt, in, l. The decrease of the levelized exergy cost for the BC turbine power output and ORC turbine power cause the decrease of the fuel-cost-related part of the system levelized exergy cost, which determined the decrease of the levelized exergy cost for the system product.

~~4.2.3.Variations of thermal parameters in ERC.~~

The influence of ejector primary inlet pressure (Pej, in) on the output and the exergy efficiency of the system are shown in Fig. 14. Thermal parameter changes in the ERC can’t affect the thermodynamic performance of the CBC and DORC. Thus, the net power output of the two cycles remain unchanged. With the increase of the ejector primary inlet pressure, the power consumption of pump 4 increases, leading to the slight decrease of the power output of the whole system.

~~Since the entrainment ratio of the ejector increases with the increase of the ejector primary inlet pressure. More working fluid in the is entrained to the ejector from the ejector secondary inlet. Thus, the mass flow rate of the working fluid in the evaporator increases, leading to the increase of the cooling capacity.~~

The increase of the ejector primary inlet pressure causes the increase of the entrainment ratio of the ejector. Thus, more secondary flow is entrained to the ejector from the evaporation, leading to the increase of the cooling capacity.

With the increase of the ejector primary inlet pressure, the power consumption of pump 4 increases gradually. At first, the exergy loss in pump 4 is smaller than the exergy produced by the cooling capacity. Then, with the increase of the pump power consumption, the exergy loss in pump 4 becomes larger than the cooling exergy increase. Thus, the exergy efficiency for the system increases at first and then decreases with the increase of the ejector primary inlet pressure.

The influence of the ejector primary inlet pressure on the levelized exergy cost and the system capital cost of the system are presented in Fig. 15. The increase of the ejector primary inlet pressure can’t affect the power output of the BC turbine and the ORC turbine. Thus, the levelized exergy cost for the BC turbine and the ORC power output remain unchanged.

The increase of the pump power consumption results in the increase of the pump 4 cost. The increase of the mass flow rate in the evaporator causes the increase of the evaporator cost. Thus, the system capital cost increases, which leads to the increase of the capital-cost-related part of cproduct. As a result, the levelized exergy cost for the system increases.

~~4.3. System optimization~~

The parametric analysis reveals the potential of optimization for the CCP system. With the increase of the BC turbine inlet temperature, the net power output of the system increases while the cooling capacity decreases. With the increase of the inlet temperature at the high-pressure side of ORC turbine, the net power output of the system decreases while the cooling capacity increases. In this study, seven key parameters (BC turbine inlet temperature, BC turbine inlet pressure, inlet temperature at the high-pressure side of ORC turbine, inlet pressure at the high-pressure side of ORC turbine, inlet temperature at the low-pressure side of ORC turbine, inlet pressure at the low-pressure side of ORC turbine and the ejector primary inlet pressure) are chosen as the variables to optimize the system. The ranges of these parameters are listed in Table 6.

Considering that the levelized exergy cost reflects the thermodynamic and the exergoeconomic aspect of the system, the levelized exergy cost for the system product is selected as the objective function and genetic algorithm is selected to conduct the single-objective optimization.

Genetic algorithm (GA) is an optimization method based on the natural biological evaluation. [45] It simulates the natural genetic rules and searches the optimization result in all the generation. The control parameters of the GA are listed in Table 7.

The optimization results of GA are listed in Table 8. It can be obtained that the minimum levelized exergy cost for the system product cproduct is 53.25 $(MWh)-1. The net power output, exergy efficiency of the CCP system are 374.37 kW, 37.31% respectively. The inlet pressure at the high-pressure side of ORC turbine is 1.85 MPa. Meanwhile, it can be evidenced from Fig. 8 and 9 that the highest output power (about 374.37 kW), exergy efficiency (about 37.31%) and the lowest levelized exergy cost (about 53.25 $(MWh)-1) at the highest inlet pressure at the high-pressure side ORC turbine (about 1.85 MPa). The inlet pressure at the high-pressure side ORC turbine is varied while other sex parameters are kept as constants in Fig. 8 and 9. Thus, inlet pressure at the high-pressure side ORC turbine plays a more important role than other six parameters when determining the performance of the system.

Fig. 16 shows the exergy destruction of different components of the system under the optimization conditions. The largest exergy destruction takes place in the ORC turbine (41.26%), which is mainly caused by the mixing of the high-pressure vapor and the low-pressure vapor. Gas heater contributes 13.44% of the total exergy destruction. Three vapor generators take up 4.13%, 11.67% and 3.73% of the exergy destruction, respectively. The exergy destruction for the ejector is 5.61%, which is also caused by the working fluid mixing. For BC turbine, condenser 1, precooler and preheater, the exergy destruction are 3.31%, 4.64%, 3.69% and 3.65%, respectively. Other components contribute to the rest 4.87% of the exergy destruction.

## Conclusion

In this paper, a combined cooling and power system is developed. Seven parameters are selected to analyze the thermodynamic and exergoeconomic performance of the system. Single-objective optimization is carried out with the help of GA. The conclusions of the study are presented as follows:

1. In the CBC, the increase of TBt,in and PBt, in contribute to the increase of the system exergy efficiency and the decrease of the levelized exergy cost for the system product.
2. In the DORC, the increase of TOt, in and TOt, in, l would cause the decrease of the system exergy efficiency and the increase of the levelized exergy cost for the system product. Meanwhile, the increase of POt, in, h and POt, in, l would result in the increase of the exergy efficiency and the decrease of the levelized exergy cost.
3. In the ERC, the increase of Pej, in would cause the increase of the refrigeration capacity and the decrease of the system net power output.
4. Single -objective optimization results show that the minimum levelized exergy cost for the system product is obtain as 53.25 $(MWh)-1 with net power output of 374.37 kW, cooling capacity of 188.63 kW and system exergy efficiency of 37.31%.
5. The inlet pressure at the high-pressure side ORC turbine plays a more important role than other six parameters on the performance of the system.

**Acknowledgement**

The authors gratefully acknowledge the financial support by the National Natural Science Foundation of China (Grant No. 51476121)

**Appendix A**

This section shows the calculation of the heat transfer area in the heat exchangers used in this study.

All the heat exchangers used in this study are shell-and-tube heat exchanger. The thermodynamic properties of the working fluid vary with the heat transfer process. Thus, to calculate the heat transfer area actually, the heat transfer processes are discretized into a lot of small sections. In each section, the heat transfer area is small and the thermodynamic properties are assumed to be constant.

For each section the heat transfer area is calculated as:

 (B1)

where Ti is the log-mean temperature difference (LMTD) and Ui is the overall heat transfer coefficient.

 (B2)

In Eq. (B2) δ and λ represent the thickness of the tube and the thermal conductivity of the tube wall, respectively. αt,i is the convection heat transfer coefficient in the tube side and αs,i is the convection heat transfer coefficient in the shell side.

For different heat transfer process, the convection heat transfer coefficient has different format. We classify the heat transfer processes into single-phase heat transfer process and two-phase heat transfer process. In gas heater, precooler and the preheater, single-phase heat transfer process happens. In evaporator, two-phase heat transfer process occurs. In vapor generators and the condensers, both the single-phase and the two-phase heat transfer process happen.

In the single-phase heat transfer process, the convection heat transfer coefficient in the tube side and the shell side are expressed as [46]:

 (B3)

 (B4)

In Eq. (B3), the Nusselt number is calculated as [47,48]:

 (B5)

 (B6)

where f is the Darcy ~~frication~~ friction factor, Re is the Reynolds and Pr is the Prandtl number.

In Eq. (B4), Des is the equivalent diameter of the shell, being expressed as:

 (B7)

where Pt is the center distance between the tubes.

Evaporation and condensation are two different two-phase heat transfer processes. In this study, the cold organic working fluid flows in the tubes of the heat exchangers. The convection heat transfer coefficient of evaporation and condensation are expressed as [49,50]:

 (B8)

 (B9)

In Eq. (B9), Pr is the reduced pressure. In Eq. (B8) Bo is the boiling number, being expressed as:

 (B10)

**Appendix B**

The constants for component capital cost calculation are list in Table B1.

**Reference**

[1] Liu P, Shu G, Tian H, Wang X, Yu Z. Alkanes based two-stage expansion with interheating Organic Rankine cycle for multi-waste heat recovery of truck diesel engine. Energy 2018; 147:337-50.

[~~1~~2] Heywood J. B. Internal combustion engine fundamentals. New York: McGraw-Hill; 1988.

~~[2] Chao H, Chao L, Hong G, Hui X, You L, Shuang W. The optimal evaporation temperature and working fluids for subcritical Organic Rankine Cycle. Energy 2012; 38: 136-143.~~

~~[3] Bombarda P, Invernizzi C, Pietra C. Heat recovery from Diesel engines: A thermodynamic comparison between Kalina and ORC cycles.~~ ~~Applied Thermal Engineering 2010; 30: 212-219.~~

~~[4] Kalyan K, Pedro J, Sundar R.~~ ~~Analysis of exhaust waste heat recovery from a dual fuel low temperature combustion engine using an Organic Rankine Cycle. Energy 2010; 35: 2387-2399.~~

~~[5]~~ ~~Wei M, Fang J, Ma C, Danish S. Waste heat recovery from heavy-duty diesel engine exhaust gases by medium temperature ORC system. Science China Technological Sciences 2011; 54: 2746-2753.~~

~~[6]~~ ~~Srinivasan K, Mago P, Zdaniuk G, Chamra L, Midkiff K. Improving the Efficiency of the Advanced Injection Low Pilot Ignited Natural Gas Engine Using Organic Rankine Cycles. 2008; 130: 022201.~~

~~[7] Tian H, Shu G, Wei H, Liang X, Liu L. Fluids and parameters optimization for the organic Rankine cycles (ORCs) used in exhaust heat recovery of Internal Combustion Engine (ICE). Energy 2012; 47: 125-136.~~

[3] Wang J, Yan Z, Wang M, Ma S, Dai Y. Thermodynamic analysis and optimization of an (organic Rankine cycle) ORC using low grade heat source. Energy 2013; 49:356-65.

[4] Lu Y, Roskilly A, Jiang L, Yu X. Working fluid selection for a small-scale organic Rankine cycle recovering engine waste heat. Energy Procedia 2017; 123:346-52.

[5] Rijpkema J, Munch K, Andersson S. Thermodynamic potential of twelve working fluids in Rankine and flash cycles for waste heat recovery in heavy duty diesel engines. Energy 2018; 160:996-1007.

[6] Su X, Shedd T A. Towards working fluid properties and selection of Rankine cycle based waste heat recovery (WHR) systems for internal combustion engines – A fundamental analysis. Appl Therm Eng 2018; 142:502-10.

[~~8~~7] Vaja I, Gambarotta A. Internal Combustion Engine (ICE) bottoming with Organic Rankine Cycles (ORCs). Energy 2010; 35(2):1084-93.

[8] Kim M, Shin G, Kim G, Cho B. Single-loop organic Rankine cycle for engine waste heat recovery using both low-and high-temperature heat sources. Energy 2016; 96:482-94.

[9] Ringer J, Seifert M, Guyotot V, Hübner W. Rankine cycle for waste heat recovery of IC engines. SAE. 2009. 2009-01-0174.

[10] Wang X, Shu G, Tian H, Liu P, Jing D, Li X. Dynamic analysis of the dual-loop Organic Rankine Cycle for waste heat recovery of a natural gas engine. Energy Convers Manage 2017; 148:724-736.

[11] Wang E, Yu Z, Zhang H, Yang F. A regenerative supercritical dual-loop organic Rankine cycle system for energy recovery from the waste heat of internal combustion engines. Appl Energy 2017; 190:574-90.

[12] Huang H, Zhu J, Deng W, Ouyang T, Yan B, Yang X. Influence of exhaust heat distribution on the performance of dual-loop organic Rankine Cycle (DORC) for waste heat recovery. Energy 2018; 151:54-65.

[13] Rajabloo T, Bonalumi D, Lora P. Effect of a partial thermal decomposition of the working fluid on the performances of ORC power plants. Energy 2017; 133:1013-26.

[14] Shi L, Shu G, Tian H, Deng S. A review of modified Organic Rankine cycles (ORCs) for internal combustion engine waste heat recovery (ICE-WHR). Renew Sustain Energy Rev 2018; 92:95-110.

[15] Xia J, Wang J, Zhang G, Lou J, Zhao P, Dai Y. Thermo-economic analysis and comparative study of transcritical power cycles using CO2-based mixtures as working fluids. Appl Therm Eng 2018; 144:31-44.

[16] Shu G, Gao Y, Tian H, Wei H, Liang X. Study of mixtures based on hydrocarbons used in ORC (organic Rankine cycle) for engine waste heat recovery. Energy 2014; 74:428-38.

[~~20~~17] Miller E, Hendricks T, Wang H, Peterson R. Integrated dual-cycle energy recovery using thermoelectric conversion and an organic Rankine bottoming cycle. Proceedings of the Institution of Mechanical Engineers, Part A: J Power Energy 2011; 225:33-43.

[~~21~~18] Shu G, Wang X, Tian H. Theoretical analysis and comparison of Rankine cycle and different organic Rankine cycles as waste heat recovery system for a large gaseous fuel internal combustion engine. Appl Therm Eng 2016; 108:525-37.

[19] Yu G, Shu G, Tian H, Huo Y, Zhu W. Experimental investigations on a cascaded steam-/organic-Rankine-cycle (RC/ORC) system for waste heat recovery (WHR) from diesel engine. Energy Convers Manage 2016; 129:43-51.

[20] Zhang C, Shu G, Tian H, Wei H, Liang X. Comparative study of alternative ORC-based combined power systems to exploit high temperature waste heat. Energy Convers Manage 2015; 89:541-54.

[21] Cao Y, Rattner AS, Dai Y. Thermoeconomic analysis of a gas turbine and cascaded CO2 combined cycle using thermal oil as an intermediate heat-transfer fluid. Energy 2018; 162:1253-68.

[~~24~~22] Ma J, Liu L, Zhu T, Zhang T. Cascade utilization of exhaust gas and jacket water waste heat from an Internal Combustion Engine by a single loop Organic Rankine Cycle system. Appl Therm Eng 2016; 107:218-26.

[23] Zhang H G, Wang E H, Fan B Y. A performance analysis of a novel system of a dual loop bottoming organic Rankine cycle (ORC) with a light-duty diesel engine. Applied Energy 2013;102: 1504-1513.

[24] Yang F, Cho H, Zhang H, Zhang J. Thermoeconomic multi-objective optimization of a dual loop organic Rankine cycle (ORC) for CNG engine waste heat recovery. Applied Energy 2017; 205: 1100-1118.

[25] Song J, Gu C. Parametric analysis of a dual loop Organic Rankine cycle (ORC) system for engine waste heat recovery. 2015; 105:995-1005.

[~~23~~26] Yu G, Shu G, Tian H, Wei H, Liu L. Simulation and thermodynamic analysis of a bottoming Organic Rankine Cycle (ORC) of diesel engine (DE). Energy 2013; 51:281-90.

[27] Li Fan, Sun Bo, Zhang C, Zhang L. Operation optimization for combined cooling, heating, and power system with condensation heat recovery. Appl Energy 2018; 230:305-16.

[28] Yari Mortaza, Ariyanfar Leyli, Aghdam EA. Analysis and performance assessment of a novel ORC based multigeneration system for power, distilled water and heat. Renew Energy 2018; 119:262-81.

[29] Bai Z, Liu T, Liu Q, Lei J, Gong L, Jin H. Performance investigation of a new cooling, heating and power system with methanol decomposition based chemical recuperation process. Appl Energy 2018; 229: 1152-63.

[~~25~~30] Chen Y, Han W, Jin H. Investigation of an ammonia-water combined power and

cooling system driven by the jacket water and exhaust gas heat of an internal combustion engine. International Journal of Refrigeration 2017; 82: 174-188.

[~~26~~31] Salek F, Moghaddam A, Naserian M. Thermodynamic analysis of diesel engine coupled with ORC and absorption refrigeration cycle. Energy Conversion and Management 2017; 140: 240-246.

[~~27~~32] Wang J, Dai Y, Sun Z. A theoretical study on a novel combined power and ejector refrigeration cycle. Int J Refrig 2009; 32(6):1186-94.

[~~29~~33] Dai Y, Wang J, Gao L. Parametric optimization and comparative study of organic Rankine cycle (ORC) for low grade waste heat recovery. Energy Convers Manage 2009; 50:576-82.

[~~30~~34] Shu G, Zhao M, Tian H, Huo Y, Zhu W. Experimental comparison of R123 and R245fa as working fluids for waste heat recovery from heavy-duty diesel engine. Energy 2016; 115:756-69.

[~~31~~35] Zhang J, Zhang H, Yang K, Yang F, Wang Z, Zhao G, Liu H, Wang E, Yao B. Performance analysis of regenerative organic Rankine cycle (RORC) using the pure working fluid and the zeotropic mixture over the whole operating range of a diesel engine. Energy Convers Manage 2014; 84:282-94.

[~~32~~36] ~~Adrian Bejan GT, Moran Michael~~ Bejan A, Tsatsaronis G, Moran M. Thermal design and optimization. New York: John Wiley & Sons; 1996.

[~~33~~37] Turton R, Bailie RC, Whiting WB, Shaeiwitz JA. Analysis, synthesis, and design of chemical processes. 3rd ed. Upper Saddle River, N.J: Prentice Hall; 2009.

~~[34] Li J, Ge Z, Liu Q, Duan Y, Yang Z. Thermo-economic performance analyses and comparison of two turbine layouts for organic Rankine cycles with dual-pressure evaporation. Energy Conversion and Management, 2018; 164: 603-614.~~

~~[35]~~ [~~http://www.chemengonline.com/pci-home~~](http://www.chemengonline.com/pci-home)

[38] Xia J, Wang J, Zhou K, Zhao P, Dai Y. Thermodynamic and economic analysis and multi-objective optimization of a novel transcritical CO2 Rankine cycle with an ejector driven by low grade heat source. Energy 2018; 161:337-51.

[~~36~~39] Sheng Z, Huai W, Tao G. Performance comparison and parametric optimization of subcritical organic Rankine cycle (ORC) and transcritical power cycle system for low-temperature geothermal power generation. Appl Energy 2011;88(8):2740-54.

[~~37~~40] Tempesti D, Fiaschi D. Thermo-economic assessment of a micro CHP system fueled by geothermal and solar energy. Energy 2013; 58: 45-51.

[~~38~~41] Velez F, Segovia JJ, Martin MC, Antonlin G, Chejne F, Quijano A. A technical, economical and market review of organic Rankine cycles for the conversion of low-grade heat for power generation. Renew Sustain Energy Rev 2012; 16:4175-89.

[~~39~~42] Akbari D, Mahmoudi M. Thermoeconomic analysis & optimization of the combined supercritical CO2 (carbon dioxide) recompression Brayton/ organic Rankine cycle. Energy 2014; 78:501-12.

[~~40~~43] Zare V, Mahmoudi M, Yari M. An exergoeconomic investigation of waste heat recovery from the Gas Turbine-Modular Helium Reactor (GT-MHR) employing an ammonia–water power/cooling cycle. Energy 2013;61. 397-409.

[~~41~~44] Lemmon EW, Huber ML, McLinden MO. NIST standard reference database 23, reference fluid thermodynamic and transport properties (REFPROP). Version 9.1. National Institute of Standards and Technology; 2010

[~~42~~45] Wang J, Dai Y, Gao L. Parametric analysis and optimization for a combined power and refrigeration cycle. Appl Energy 2008;85(11):1071-85.

[~~43~~46] Kern DQ. Process heat transfer. New York: McGraw-Hill; 1950

[~~44~~47] Kandylas IP, Stamatelos AM. Engine exhaust system design based on heat transfer computation. Energy Convers Manage 1999; 40:1057-72.

[~~45~~48] Incropera FP, DeWitt DP. Fundamentals of heat and mass transfer. New York: Wiley; 2002

[~~46~~49] Gungor KE, Winterton RHS. Simplified general correlation for saturated flow boiling and comparisons of correlations with data. Chem Eng Res and Des, 1987; 65:148-56.

[~~47~~50] Shah MM. A general correlation for heat transfer during film condensation inside pipes. Int J Heat Mass Transf 1979; 22:547-56.

**Figure captions**

**Fig. 1.** Schematic diagram of the CCP system

**Fig. 2.** Influences of BC turbine inlet temperature on the output and the exergy efficiency of the system.

**Fig. 3.** Influences of BC turbine inlet temperature on the levelized exergy cost and the system capital cost of the system.

**Fig. 4.** Influences of BC turbine inlet pressure on the output and the exergy efficiency of the system.

**Fig. 5.** Influences of BC turbine inlet pressure on the levelized exergy cost and the system capital cost of the system.

**Fig. 6.** Influences of inlet temperature at the high-pressure side of ORC turbine on the output and the exergy efficiency of the system.

**Fig. 7.** Influences of inlet temperature at the high-pressure side of ORC turbine on the levelized exergy cost and the system capital cost of the system.

**Fig. 8.** Influences of inlet pressure at the high-pressure side of ORC turbine on the output and the exergy efficiency of the system.

**Fig. 9.** Influences of inlet pressure at the high-pressure side of ORC turbine on the levelized exergy cost and the system capital cost of the system.

**Fig. 10.** Influences of inlet temperature at the low-pressure side of ORC turbine on the output and the exergy efficiency of the system.

**Fig. 11.** Influences of inlet temperature at the low-pressure side of ORC turbine on the levelized exergy cost and system capital cost of the system.

**Fig. 12.** Influences of inlet pressure at the low-pressure side of ORC turbine on the output and the exergy efficiency of the system.

**Fig. 13.** Influences of inlet pressure at the low-pressure side of ORC turbine on the levelized exergy cost and system capital cost of the system.

**Fig. 14.** Influences of ejector primary inlet pressure on the output and the exergy efficiency of the system.

**Fig. 15.** Influences of ejector primary inlet pressure on the levelized exergy cost and the system capital cost of the system.

**Fig. 16.** Exergy destruction of different components

**Table 1** Energy and exergy models for each component in CCP system

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Component | Energy equation | EF | EP | ED | EL |
| Gas heater |  |  |  |  | / |
| BC turbine |  |  |  |  | / |
| Vapor generator 2 |  |  |  |  | / |
| Precooler |  | / | / |  |  |
| Compressor |  |  |  |  | / |
| Vapor generator 1 |  |  |  |  | / |
| ORC turbine |  |  |  |  | / |
| Condenser 1 |  | / | / |  |  |
| Pump 1 |  |  |  |  | / |
| Preheater |  |  |  |  | / |
| Pump 2 |  |  |  |  | / |
| Pump 3 |  |  |  |  | / |
| Vapor generator 3 |  |  |  |  | / |
| Condenser 2 |  | / | / |  |  |
| Valve |  | / | / |  | / |
| Pump 4 |  |  |  |  | / |
| Ejector |  |  |  |  | / |
| Evaporator |  |  |  |  | / |

**Table 2** Cost balance and auxiliary relation [30] for each component of CCP system

|  |  |  |
| --- | --- | --- |
| Component | Cost balance | Auxiliary relation |
| Gas heater |  | cg1=cg2=0 |
| Vapor generator 2 |  | c4=c5 |
| BC turbine |  | c4=c3 |
| Precooler |  | c1=c5 |
| Compressor |  | celec,1=cBt |
| Vapor generator 1 |  | cg2=cg3 |
| ORC turbine |  | c10=c11=c12 |
| Pump 1 |  | celec,3=cOt |
| Condenser 1 |  | c13=c12 |
| Preheater |  | cw1=cw2=0 |
| Pump 2 |  | celec,2=cOt |
| Pump 3 |  | celec,3=cOt |
| Vapor generator 3 |  | cw3=cw2 |
| Valve | / | c19=c20 |
| Pump 4 |  | celec,4=cOt |
| Condenser 2 |  | c16=c17 |
| Ejector |  | / |
| Evaporator |  | c20=c21 |

**Table 3** Main parameters of the engine [7]

|  |  |
| --- | --- |
| Parameters | Value |
| Power output (kW) | 2928 |
| Rotation (r(min)-1) | 1000 |
| Exhaust gas temperature (℃ ) | 470 |
| Exhaust gas mass flow rate (kg s-1) | 4.35 |
| Temperature of jacket water (℃ ) | 90/79 |
| Mass flow rate of jacket water (kg s-1) | 25 |

**Table 4** Composition of the exhaust gas [7]

|  |  |  |
| --- | --- | --- |
| Composition | Molecular (g(mol)-1) | Fraction (%) |
| O2 | 32.00 | 9.3 |
| CO2 | 44.00 | 9.1 |
| H2O | 18.01 | 7.4 |
| N2 | 28.01 | 74.2 |

**Table 5** Condition of simulation for the CCP system

|  |  |
| --- | --- |
| Parameter | Value |
| Ambient temperature (℃ ) | 20 |
| Ambient pressure (MPa) | 0.101 |
| Compressor inlet temperature (℃ ) | 35 |
| BC turbine inlet temperature (℃ ) | 400 |
| BC turbine inlet pressure (MPa) | 18 |
| BC turbine outlet pressure (MPa) | 8 |
| Inlet temperature at the high-pressure side of ORC turbine (℃ ) | 150 |
| Inlet pressure at the high-pressure side of ORC turbine (MPa) | 1.6 |
| Inlet temperature at the low-pressure side of ORC turbine (℃ ) | 100 |
| Inlet pressure at the low-pressure side of ORC turbine (MPa) | 1.0 |
| Outlet pressure of pump 1 (MPa) | 0.9 |
| Ejector primary inlet pressure (MPa) | 0.4 |
| Terminal temperature difference at gas heater outlet (℃ ) | 100 |
| Pinch point temperature difference in vapor generator 1 (℃ ) | 30 |
| Pinch point temperature difference in vapor generator 2 (℃ ) | 30 |
| Pinch point temperature difference in vapor generator 3 (℃ ) | 25 |
| Condensation temperature of condenser 1 (℃ ) | 30 |
| Condensation temperature of condenser 2 (℃ ) | 30 |
| Evaporation temperature of evaporator (℃ ) | 5 |
| Isentropic efficiency of BC turbine (%) | 80 |
| Isentropic efficiency of ORC turbine (%) | 80 |
| Isentropic efficiency of compressor (%) | 80 |
| Isentropic efficiency of pump 1 (%) | 75 |
| Isentropic efficiency of pump 2 (%) | 75 |
| Isentropic efficiency of pump 3 (%) | 75 |
| Inlet temperature of cooling water (℃ ) | 20 |

**Table 6** Parameters for GA

|  |  |
| --- | --- |
| Parameter | Operation range |
| BC turbine inlet temperature (℃ ) | 330-440 |
| BC turbine inlet pressure (MPa) | 15-20 |
| Inlet temperature at the high-pressure side of ORC turbine (℃ ) | 130-180 |
| Inlet pressure at the high-pressure side of ORC turbine (MPa) | 1.4-2 |
| Inlet temperature at the low-pressure side of ORC turbine (℃ ) | 90-150 |
| Inlet pressure at the low-pressure side of ORC turbine (MPa) | 0.9-1.3 |
| Ejector primary inlet pressure (MPa) | 0.3-1 |

**Table 7** Control parameters of GA


|  |  |
| --- | --- |
| Tuning parameters | Value |
| Population size | 20 |
| Mutation probability | 0.01 |
| Crossover probability | 0.8 |
| Stop generation | 200 |

**Table 8** Single-objective optimization results

|  |  |
| --- | --- |
| Parameter | Value |
| BC turbine inlet temperature (℃ ) | 425.46 |
| BC turbine inlet pressure (MPa) | 20.00 |
| Inlet temperature at the high-pressure side of ORC turbine (℃ ) | 144.32 |
| Inlet pressure at the high-pressure side of ORC turbine (MPa) | 1.85 |
| Inlet temperature at the low-pressure side of ORC turbine (℃ ) | 100.03 |
| Inlet pressure at the low-pressure side of ORC turbine (MPa) | 1.26 |
| Ejector primary inlet pressure (MPa) | 0.54 |
| Net power output (kW) | 374.37 |
| Cooling capacity (kW) | 188.63 |
| Exergy efficiency (%) | 37.31 |
| Levelized exergy cost ($ (MWh)-1) | 53.25 |

**Table B1** Constants for component costs [37]

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Constant | Value | Constant | Value | Constant | Value |
| B1,he | 1.63 | K3,pump | 0.1538 | C3,he | 0.08183 |
| B2,he | 1.66 | K1,turb | 2.7051 | C1,pump | -0.3635 |
| B1,pump | 1.89 | K2,turb | 1.4398 | C2,pump | 0.3957 |
| B2,pump | 1.35 | K3,turb | -0.1776 | C3,pump | -0.0026 |
| K1,he | 4.3247 | K1,comp | 2.2897 | FM,he | 1.0 |
| K2,he | -0.3030 | K2,comp | 1.3604 | FBM,turb | 3.5 |
| K3,he | 0.1634 | K3,comp | -0.1027 | FBM,comp | 2.7 |
| K1,pump | 3.3892 | C1,he | 0.03881 | FM,pump | 2.2 |
| K2,pump | 0.0536 | C2,he | -0.11272 |  |  |



**Fig. 1.** Schematic diagram of the CCP system



**Fig. 2.** Influences of BC turbine inlet temperature on the output and the exergy efficiency of the system.



**Fig. 3.** Influences of BC turbine inlet temperature on the levelized exergy cost and the system capital cost of the system.



**Fig. 4.** Influences of BC turbine inlet pressure on the output and the exergy efficiency of the system.



**Fig. 5.** Influences of BC turbine inlet pressure on the levelized exergy cost and the system capital cost of the system.



**Fig. 6.** Influences of inlet temperature at the high-pressure side of ORC turbine on the output and the exergy efficiency of the system.



**Fig. 7.** Influences of inlet temperature at the high-pressure side of ORC turbine on the levelized exergy cost and the system capital cost of the system.



**Fig. 8.** Influences of inlet pressure at the high-pressure side of ORC turbine on the output and the exergy efficiency of the system.



**Fig. 9.** Influences of inlet pressure at the high-pressure side of ORC turbine on the levelized exergy cost and the system capital cost of the system.



**Fig. 10.** Influences of inlet temperature at the low-pressure side of ORC turbine on the output and the exergy efficiency of the system.



**Fig. 11.** Influences of inlet temperature at the low-pressure side of ORC turbine on the levelized exergy cost and system capital cost of the system.



**Fig. 12.** Influences of inlet pressure at the low-pressure side of ORC turbine on the output and the exergy efficiency of the system.




**Fig. 13.** Influences of the inlet pressure at the low-pressure side of ORC turbine on the levelized exergy cost and system capital cost of the system.



**Fig. 14.** Influences of ejector primary inlet pressure on the output and the exergy efficiency of the system.



**Fig. 15.** Influences of ejector primary inlet pressure on the levelized exergy cost and the system capital cost of the system.



**Fig. 16.** Exergy destruction of different components